SPECIFICATION SECTION XXX

PRODUCT: COMMERCIAL REVERSE OSMOSIS SYSTEM

1.0 GENERAL	Furnish a commercial reverse osmosis system (RO) as specified here in this section and as called for in the equipment schedule for the reduction of total dissolved solids. The RO shall be supplied complete, and assembled entirely by one manufacturer. The system shall include all components required for proper operation of the system. These components include system control package, flow meters, high pressure pump, membranes, pre-filter, adjustment valves, pressure gauges, automatic inlet valve, and frame. The RO shall be a Watts Pure Water brand model number PWR2511____ manufactured by Watts.

2.0 RELATED SECTIONS	XXX

3.0 COMPONENTS

3.1 System Support Frame

All components of the reverse osmosis (RO) system will be mounted on a single support frame. The support frame shall be constructed of a one piece broke 304 stainless steel panel measuring .10” in thickness. The support frame shall be suitable for wall mounting and shall also allow for the addition of mounting legs for independent floor mounting.

3.2 Pre Filter

The pre-filter housing shall be a single element type constructed of FDA grade reinforced polypropylene and certified to NSF/ANSI standard 42. The housing will have a 125 PSI maximum working pressure and a maximum temperature rating of 125 deg. F (51 deg. C). The housing will have 1/2” NPT inlet and outlet and accept a 2 ½” X 10” single replaceable filter cartridge element. The housing will be sized to flow 5 GPM at a pressure drop of 3 PSI using a five micron melt blown cartridge. The replaceable filter elements shall be a melt blown fiber type five micron nominally rated cartridge certified to NSF/ANSI Standard 42. The filter shall be constructed of 100% polypropylene to resist the growth of microbiologic films.

3.3 High Pressure Pump

A high pressure pump will be provided, mounted on the RO frame, to boost the membrane feed water pressure to a maximum of 250 psi. The pump shall be a rotary vane type constructed of brass and rated for 140 gallons per hour. The pump will have a built in relief valve factory adjusted to 250 psi relief pressure.  The motor shall have an ODP motor housing and shall be dual voltage rated for 110/220 volt single phase. The motor must be ½ horse power rated for 150, 250, 600, and 1200 gallon per day production systems to ensure adequate membrane feed water volume and pressure.

3.4 Membrane and Membrane Housings

The membrane housings shall be constructed of 316L stainless steel for superior corrosion resistance, with glass reinforced polypropylene end caps. The maximum operating pressure of the housings shall be 300 psi with a 1000 psi burst pressure. The housing’s maximum operating temperature will be 100 deg. F (37 deg. C). Membranes shall be Watts brand high rejection thin film composite 2.5” diameter. Membranes must have a minimum average salt rejection of 95% under the standard test conditions of 225 psi feed pressure, and 77 deg F (25 deg. C) , with a 2000 ppm Na Cl feed solution at a pH of 7.0.

3.5 System Controls

The system will include electronic and hydraulic controls for automatic operation and manual adjustment. The electronic controller shall be a micro processor based controller with inputs and outputs for automation of the RO components. Input signal shall be: low feed water pressure. Output signals shall be: open/close automatic inlet valve and start/stop high-pressure pump. The controller shall have the option of a 5 minute and a 30 minute delayed automatic restart after a low feed water pressure shut down to prevent on off cycling of the system during a low feed water pressure condition. The controller will have a toggle switch for manual on off control of the system. The RO system will have an adjustable time automatic fast flush feature consisting of a flush timer and brass soleniod valve to aid in cleaning sediment off of the membrane surface. The automatic inlet valve will be a brass solenoid valve rated for 200 psi working pressure with 120V coil. A normally closed pressure switch and stainless steel check valve will be mounted on the permeate line of the RO for automatic on off of the system when used in conjunction with a bladder tank. Manual hydraulic control valves will be provided on the RO system to regulate reject recycle volume and reject water volume. The reject water and recycle water valves shall be needle valves, constructed of brass, and rated for 600 psi maximum working pressure and have a temperature rating of up to 500 deg. F (260 deg. C).

3.6 Flow indicators and Gauges

The RO system will be supplied with pressure gauges to indicate the pressure of the pre-filter inlet, pre-filter outlet, and pump discharge water. All pressure gauges shall have an acrylic window. The pump discharge pressure gauge will be glycerine filled. Flow meters will be provided to give an indication of product and reject water flow rates. Flow meter flow rate scales are to be calibrated to gallons per minute and liters per minute within 3 percent accuracy. Flow meters shall be variable area inline type with disconnects at each end to ease internal cleaning of the meter body. Meter bodies are to be constructed of polysulfone or acrylic with 316 stainless steel float and float rod and viton orings. Prefilter inlet, outlet, and pump discharge pressure gauges and all flow meters are to be mounted next to the electronic controller so that all are in plain view of the operator while the system is running.

3.7 System Piping

High pressure pump discharge piping shall be constructed of high density polyethylene tubing rated for 375 psi working pressure. Reject, recycle, and permeate water piping shall be high density polyethylene tubing.

3.8 Test Kit

Provide a Myron L model 6 P hand held water quality meter along with pH 4 and pH10 calibration solutions and conductivity KCl- 7000 (7 mS), 442-3000 TDS calibration solutions. Each calibration solution shall be provided in a one quart quantity. Also provide a silt density index test kit, Watts model number T3031, for testing RO feed water SDI.

4.0 SERVICES

4.1 Warranty

Provide a 1 year parts and labor warranty for the system to protect against manufacturers defects. System shall not be subjected to water temperatures above 100 deg. F (37 deg. C), below 35 deg. F (2 deg. C), iron, hardness, or chlorine.

4.2 Start Up

The Contractor providing the equipment shall provide start up of the RO system, a complete set of operating, maintenance, and installation instructions, one complete set of spare pre-filter cartridges for the pre-filter housing, and operator training.